## Sheet1
dm@mevronprocess.com
The capacity of a low pressure natural gas (less than 1 psi, 6.9 kPa) pipe line with a small pressure drop can be calculated with the Spitzglass formula
q = 3550 k ( h / l SG)1/2 (1)
where | Flow | q | 41.8395 | ft3h | 1.1848 | m3h | 1 | Meter | 1 | Kg
| Dia | d | 8 | inch |  |  | 3.2808 | Feet | 2.2046 | LB
q = natural gas flow capacity (cfh) | Length | l | 3280.8399 | ft
| Sp. Gravity | SG | 7.3 | Kg/M3 | 0.45572 | lb/ft3 | 35.3147 | ft3
h = pressure drop (in Water Column) |  | k | 150.3292 |  |  |  | Pressure drop 1" Water Column considered
l = length of pipe (ft)
k = [d5 / (1 + 3.6 / d + 0.03 d)]1/2
d = inside diameter pipe (in)
SG = specific gravity
For natural gas the nominal BTU/cf varies from about 900 to 1100 BTU/cf. In general it is common to set
1 Cubic Foot (CF) = approx 1,000 BTUs
1 CFH = 1 MBH
The specific gravity of natural gas varies from 0.55 to 1.0.
Example - Natural Gas Pipe Capacity
The capacity of a 100 ft natural gas pipe with a nominal diameter 0.5 inches (actual ID 0.622 in) and 0.5 inches WC pressure drop can be calculated as
k = [((0.622 in))5/(1 + 3.6 / (0.622 in) + 0.03 (0.622 in))]1/2
0.117
q = 3550 0.117 ((0.5 in) / (100 ft) 0.60 )1/2
= 37.9 (cfh)
Specific gravity of natural gas is set to 0.60.